## Workbook Test3 Test.csv
Category | Event | Keypad Text | Size | Ras Text | Size | Contact ID | SIA | Parameter 1 | Parameter 2 | Parameter 3 | Parameter 4 | Parameter 5 | Parameter 6 | Comments
Alarm | 1 | Fire Zone Alarm | 15 | Fire Zone Alarm | 15 | E110-GG-Zn### Fire | [FA] Fire | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 2 | 24Hr Tamper Zone Alarm | 22 | 24Hr Tamper Zone Alarm | 22 | E137-GG-Zn### Tamper | [TA] Alarm Equipment Tamper | P1 Zone | P2 Module | P3 | P4 | P5 | P6 | Zone programmed as tamper
Alarm | 3 | Hold-Up Zone Alarm | 18 | Hold-Up Zone Alarm | 18 | E122-GG-Zn### Silent Alarm | [HA] Hold-Up | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 4 | Medical Zone Alarm | 18 | Medical Zone Alarm | 18 | E100-GG-Zn### Medical | [MA] Medical | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 5 | Panic Zone Alarm | 16 | Panic Zone Alarm | 16 | E120-GG-Zn### Panic Alarm | [PA] Panic | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 6 | 24Hr Burglary Zone Alarm | 24 | 24Hr Burglary Zone Alarm | 24 | E133-GG-Zn### 24Hr Burglary | [BA] Burglary | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 7 | Burglary Zone Alarm | 19 | Burglary Zone Alarm | 19 | E130-GG-Zn### Burglary | [BA] Burglary | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 8 | Entry Alarm | 11 | Delay 1 or Delay 2 Zone Alarm | 29 | E134-GG-Zn### Entry/Exit | [BA] Burglary | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 9 | Exit Error Alarm | 16 | Exit Error Alarm | 16 | E374-GG-Zn### Exit Error Restore | [EE] Exit Error (User) | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 10 | Fire Zone Restored | 18 | Fire Zone Alarm Restored | 24 | R110-GG-Zn### Fire Restore | [FH] Fire Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 11 | 24Hr Tamper Zone Restored | 25 | 24Hr Tamper Zone Alarm Restored | 31 | E137-GG-Zn### Tamper | [TR] Alarm Equip Tamper Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6 | Zone programmed as tamper
Alarm | 12 | Hold-Up Zone Restored | 21 | Hold-Up Zone Alarm Restored | 27 | R122-GG-Zn### Silent Restore | [HH] Hold-Up Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 13 | Medical Zone Restored | 21 | Medical Zone Alarm Restored | 27 | R100-GG-Zn### Medical | [MH] Medical Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 14 | Panic Zone Restored | 19 | Panic Zone Alarm Restored | 25 | R120-GG-Zn### Panic Restore | [PH] Panic Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 15 | 24Hr Burglary Zone Rest | 23 | 24Hr Burglary Zone Alarm Restored | 33 | R133-GG-Zn### Burglary Restore | [BH] Burglary Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 16 | Burglary Zone Restored | 22 | Burglary Zone Alarm Restored | 28 | R130-GG-Zn### Burglary Restore | [BH] Burglary Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 17 | Entry Restored | 14 | Delay 1 or Delay 2 Zone Alarm Restored | 38 | R134-GG-Zn### Entry/Exit Restore | [BH] Burglary Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 18 | Fire Alarm Cross Zone | 21 | Fire Zone Cross Alarm | 21 | E110-GG-Zn### Fire Cross | [FM] Fire Cross | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 19 | Burglary Alarm Cross Zone | 25 | Burglary Alarm Cross Zone | 25 | E130-GG-Zn### Burglary | [BM] Burglary Cross | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 20 | Entry Alarm Cross Zone | 22 | Delay 1 or Delay 2 Cross Zone Alarm | 35 | E134-GG-Zn### Entry/Exit Cross | [BM] Burglary Cross | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 21 | Fire Zone Auto Bypassed | 23 | Fire Zone Auto Bypassed | 23 | E373-GG-Zn### Fire Trouble | [FT] Fire Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 22 | Fire Chamber Trouble | 20 | Fire Chamber Maintenance Alert | 30 | E393-GG-Zn### Maintenance Alert Trouble | [AS] Analogue Fire Sensor Needs Cleaning | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 23 | Tamper Zone Auto Bypassed | 25 | Tamper Zone Auto Bypassed | 25 | E380-GG-Zn### Sensor Trouble | [TT] Tamper Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 24 | Hold Up Zone Auto Bypassed | 26 | Hold Up Zone Auto Bypassed | 26 | E376-GG-Zn### Hold Up Zone Trouble | [HT] Hold Up Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 25 | Panic Zone Auto Bypassed | 24 | Panic Zone Auto Bypassed | 24 | E375-GG-Zn### Panic Zone Trouble | [PT] Panic Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 26 | Medical Zone Auto Bypassed | 26 | Medical Zone Auto Bypassed | 26 | E380-GG-Zn### Sensor Trouble | [MT] Medical Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 27 | 24Hr Burg Auto Bypassed | 23 | 24-Hr Burglary Auto Bypassed | 28 | E380-GG-Zn### Sensor Trouble | [BT] Burglary Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 28 | Entry Zone Auto Bypassed | 24 | Entry / Exit Zone Auto Bypassed | 31 | E380-GG-Zn### Sensor Trouble | [BT] Burglary Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 29 | Burg Zone Auto Bypassed | 23 | Burglary Zone Auto Bypassed | 27 | E380-GG-Zn### Sensor Trouble | [BT] Burglary Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 30 | Fire Zone Unbypassed | 20 | Fire Zone Unbypassed | 20 | R373-GG-Zn### Fire Trouble Restore | [FJ] Fire Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 31 | Fire Chamber OK | 15 | Fire Chamber Maintenance Alert Restored | 39 | R393-GG-Zn### Maintenance Alert Restore | [AN] Analogue Fire Sensor Normal | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 32 | Tamper Zone Unbypassed | 22 | Tamper Zone Unbypassed | 22 | R380-GG-Zn### Sensor Trouble Restore | [TJ] Tamper Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 33 | Hold Up Zone Unbypassed | 23 | Hold Up Zone Unbypassed | 23 | R376-GG-Zn### Hold Up Zone Trouble Restore | [HJ] Hold Up Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 34 | Panic Zone Unbypassed | 21 | Panic Zone Unbypassed | 21 | R375-GG-Zn### Panic Trouble Restore | [PJ] Panic Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 35 | Medical Zone Unbypassed | 23 | Medical Zone Unbypassed | 23 | R380-GG-Zn### Sensor Trouble Restore | [MJ] Medical Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 36 | 24Hr Burg Zone Unbypassed | 25 | 24-Hr Burglary Zone Unbypassed | 30 | R380-GG-Zn### Sensor Trouble Restore | [BJ] Burglary Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 37 | Entry/Exit Zone Unbypassed | 26 | Entry/Exit Zone Unbypassed | 26 | R380-GG-Zn### Sensor Trouble Restore | [BJ] Burglary Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 38 | Burglary Zone Unbypassed | 24 | Burglary Zone Unbypassed | 24 | R380-GG-Zn### Sensor Trouble Restore | [BJ] Burglary Trouble Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 39 | Zone Tamper | 11 | Zone Tamper Alarm | 17 | E144-GG-Zn### Sensor Tamper | [TA] Alarm Equipment Tamper | P1 Zone | P2 Module | P3 | P4 | P5 | P6 | Alarm and Tamper Monitoring Zone alarm
Alarm | 40 | Zone Tamper Restored | 20 | Zone Tamper Restored | 20 | R144-GG-Zn### Sensor Tamper | [TR] Alarm Equip Tamper Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6 | Alarm and Tamper Monitoring Zone alarm
Trouble | 41 | Fire Zone Bypassed | 18 | Fire Zone Bypassed | 18 | E571-GG-Zn### Fire Bypass | [FB] Fire Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 42 | 24Hr Zone Bypassed | 18 | 24Hr Zone Unbypassed | 20 | E572-GG-Zn### 24Hr Zone Bypass | [PB] Panic Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 43 | Burglary Zone Bypassed | 22 | Burglary Zone Bypassed | 22 | E573-GG-Zn### Burglary Bypass | [BB] Burglary Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 44 | Panic Zone Bypassed | 19 | Panic Zone Bypassed | 19 | E572-GG-Zn### 24Hr Zone Bypass | [PB] Panic Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 45 | Medical Zone Bypassed | 21 | Medical Zone Bypassed | 21 | E572-GG-Zn### 24Hr Zone Bypass | [MB] Panic Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 46 | Hold-Up Bypassed | 16 | Hold-Up Zone Bypassed | 21 | E572-GG-Zn### 24Hr Bypass | [HB] Hold-Up Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 47 | Tamper Zone Bypassed | 20 | Tamper Zone Bypassed | 20 | E572-GG-Zn### 24Hr Bypass | [TB] Tamper Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 48 | Fire Zone Unbypassed | 20 | Fire Zone Unbypassed | 20 | R571-GG-Zn### Fire Bypass Restore | [FU] Fire Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 49 | 24Hr Zone Unbypassed | 20 | 24Hr Zone Unbypassed | 20 | R572-GG-Zn### 24Hr Zone Bypass Restore | [PU] Panic Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 50 | Burglary Zone Unbypassed | 24 | Burglary Zone Unbypassed | 24 | R573-GG-Zn### Burglary Bypass Restore | [BU] Burglary Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 51 | Panic Zone Unbypassed | 21 | Panic Zone Unbypassed | 21 | R572-GG-Zn### 24Hr Zone Bypass Restore | [PU] Panic Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 52 | Medical Zone Unbypassed | 23 | Medical Zone Unbypassed | 23 | R572-GG-Zn### 24Hr Zone Bypass Restore | [MU] Panic Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 53 | Hold-Up Zone Unbypassed | 23 | Hold-Up Zone Unbypassed | 23 | R572-GG-Zn### 24Hr Bypass Restore | [HU] Hold-Up Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 54 | Tamper Zone Unbypassed | 22 | Tamper Zone Unbypassed | 22 | R572-GG-Zn### 24Hr Bypass Restore | [TU] Tamper Un Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 55 | Fire Zone Lockout | 17 | Fire Zone Lockout | 17 | E575-GG-Zn### Burglary Bypass | [BD] Burglary Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 56 | 24Hr Zone Lockout | 17 | 24Hr Zone Lockout | 17 | E575-GG-Zn### Burglary Bypass | [BD] Burglary Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 57 | Burg Zone Lockout | 17 | Burg Zone Lockout | 17 | E575-GG-Zn### Burglary Bypass | [BD] Burglary Bypass | P1 Zone | P2 Module | P3 | P4 | P5 | P6
O/C | 58 | Burglary Alarm Cancelled | 24 | Burglary Alarm Cancelled | 24 | E406-GG-Ur### Cancel | [BC] Burglary Cancel | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 59 | Fire Alarm Cancelled | 20 | Fire Alarm Cancelled | 20 | E406-GG-Ur### Cancel | [FC] Fire Cancel | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Trouble | 60 | Sensor Watch Trouble | 20 | Sensor Watch Trouble | 20 | E391-GG-Zn### Sensor Watch Trouble | [NA] No Activity | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 61 | Sensor Watch Restored | 21 | Sensor Watch Restored | 21 | R391-GG-Zn### Sensor Watch Restore | [NS] Activity Resumed | P1 Zone | P2 Module | P3 | P4 | P5 | P6
System | 62 | Test Report - Manual | 20 | Test Report - Manual | 21 | E601-GG-000 Manual Test | [RX] Test Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 63 | Test Report - Auto | 18 | Test Report - Auto | 18 | E602-GG-000 Periodic Test Report | [RP] Automatic Test | P1 Module | P2 | P3 | P4 | P5 | P6
System | 64 | Test Report - With Trouble | 26 | Test Report - With Trouble | 26 | E608-GG-Zn### Periodic Test Ð With Trouble | [RY] Test Off Normal | P1 Module | P2 | P3 | P4 | P5 | P6
System | 65 | Walk Test - Begin | 17 | Walk Test - Begin | 17 | E607-GG-Ur### Walk Test Mode | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 66 | Walk Test - Ended | 17 | Walk Test Ð Ended | 17 | R607-GG-Ur### Walk Test Mode | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Test | 67 | Zone Tested OK | 14 | Walk Test Zone OK | 17 | E611-GG-Zn### Point Test OK | [TP] Walk Tested Point OK | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Test | 68 | Zone Not Tested | 15 | Zone Not Tested During Walk Test | 32 | E612-GG-Zn### Point Not Tested | Local | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 69 | AC Power Fail | 13 | AC Power Lost or Missing | 25 | E301-00-Zn### AC Loss | [AT] AC Trouble | P1 Module | P2 | P3 | P4 | P5 | P6 | Panel and Modules have a Zn Number
Trouble | 70 | AC Power Restored | 17 | AC Power Restored | 17 | R301-00-Zn### AC Loss Restore | [AR] AC Trouble Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 71 | Low Battery | 11 | Low Battery Condition | 21 | E302-00-Zn### Low Battery | [YT] Low Battery | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 72 | Low Battery Restored | 20 | Low Battery Condition Restored | 30 | R302-00-Zn### Low Battery Restore | [YR] Low Battery Restore | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 73 | Battery Missing | 15 | Battery Missing Battery Missing Or Dead | 39 | E311-00-Zn### Battery Missing/Dead | [YM] Battery Missing | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 74 | Battery Missing Restored | 24 | Battery Missing Condition Restored | 34 | R311-00-Zn### Battery Missing/Dead | [YR] Low Battery Restore | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 75 | Checksum Error | 14 | ROM Checksum Error | 18 | E304-00-Zn### ROM Checksum Bad | [YF] Parameter Checksum Fail | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 76 | ROM Checksum Restored | 21 | ROM Checksum Restored | 21 | R304-00-Zn### ROM Checksum Bad Restore | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 77 | Communications Fail | 19 | Communications Fail Destination | 31 | E354-00-Zn### Fail To Communicate | [YC] Communications Fail | P1 Dest | P2 Module | P3 | P4 | P5 | P6 | Each Destination has a Zn# 901 to 909
Trouble | 78 | Communications Restored | 23 | Communications Fail Restored | 28 | R354-00-Zn### Communicate Restore | [YK] Communications Restore | P1 Dest | P2 Module | P3 | P4 | P5 | P6 | Each Destination has a Zn# 901 to 909
System | 79 | Date & Time Changed | 19 | Date & Time Reset | 17 | E625-GG-Ur### Date/Time Reset | [JD] Date Changed By User | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 80 | Summer Time Begin | 17 | Summer Time Begin | 17 | E625-GG-000 Date/Time Reset | [JT] Time Changed | P1 Module | P2 | P3 | P4 | P5 | P6
System | 81 | Summer Time Ended | 17 | Summer Time Ended | 17 | E625-GG-000 Date/Time Reset | [JT] Time Changed | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 82 | Telco Line Fail | 15 | Telephone Line Fail | 19 | E351-00-ZN### Telco 1 Fault | [LT] Phone Line Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 83 | Telco Line Restored | 19 | Telephone Line Restored | 23 | R351-00-ZN### Telco 1 Fault Restore | [LR] Phone Line Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 84 | Power Up Or Reset | 17 | Power Up Or Reset | 17 | E305-00-Mo### System Reset | [RR] Power Up | P1 Module | P2 Table | P3 | P4 | P5 | P6 | Table: 0=Cold, 1=Warm, 2=Watchdog
Trouble | 85 | Area Inactivity Alert | 21 | Area Inactivity Alert (No Arm/Disarm) | 37 | E654-GG-000 System Inactivity | [CD] Closing Delinquent | P1 | P2 | P3 | P4 | P5 | P6
Trouble | 86 | Area Inactive Alert Rest | 24 | Area Inactive Alert Restored | 28 | R654-GG-000 System Inactivity Restore | Local | P1 | P2 | P3 | P4 | P5 | P6
System | 87 | Service Required | 16 | Service Required | 16 | E616-00-000 Service Request | [YX] Service Required | P1 Module | P2 | P3 | P4 | P5 | P6
System | 88 | History Log Overflow | 20 | History Event Log Overflow | 26 | E624-GG-Zn### Event Log Overflow | [JO] Log Overflow | P1 Module | P2 | P3 | P4 | P5 | P6
System | 89 | History Log At 90% | 18 | History Event Log At 90% Full | 29 | E623-GG-Zn### Event Log 90% Full | [JL] Log Threshold | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 90 | LAN+ Overload | 13 | LAN+ Output Overload | 20 | E312-00-Zn### Power Supply Over Current | [YI] Over Current Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 91 | LAN+ Overload Restored | 22 | LAN+ Output Overload Restored | 29 | R312-00-Zn### Power Supply Over Current Restore | [YJ] Over Current Trouble Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 92 | ACC+ Overload | 13 | ACC+ Output Overload | 20 | E312-00-Zn### Power Supply Over Current | [YI] Over Current Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 93 | ACC+ Overload Restored | 22 | ACC+ Output Overload Restored | 29 | R312-00-Zn### Power Supply Over Current Restore | [YJ] Over Current Trouble Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 94 | COMM+ Overload | 14 | COMM+ Output Overload | 21 | E312-00-Zn### Power Supply Over Current | [YI] Over Current Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 95 | COMM+ Overload Restored | 23 | COMM+ Output Overload Restored | 30 | R312-00-Zn### Power Supply Over Current Restore | [YJ] Over Current Trouble Restore | P1 Module | P2 | P3 | P4 | P5 | P6
O/C | 96 | Invalid PIN Exceeded | 20 | Invalid PIN Retry Count Exceeded | 32 | E461-GG-Zn### Wrong Code Entry | [JA] User Code Tamper | P1 Console | P2 | P3 | P4 | P5 | P6
O/C | 97 | Service Mode Begin | 18 | Service Mode Begin | 18 | E466-GG-999 Service On Premise | [TS] Test Start | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 98 | Service Mode Ended | 18 | Service Mode Ended | 18 | R466-GG-999 Service Off Premise | [TE] Test End | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 99 | Programming Mode Begin | 22 | Programming Mode Begin | 22 | E627-GG-Zn### Program Mode Entry | [LB] Local Program | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 100 | Program Mode Ended | 18 | Program Mode Ended | 18 | E628-GG-Zn### Program Mode Exit | [LX] Local Programming Ended | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Trouble | 101 | Program Data Changed | 20 | Control Panel Program Changed | 29 | E306-00-Zn### Program Changed | [YG] Parameter Changed | P1 Module | P2 | P3 | P4 | P5 | P6
O/C | 102 | Auto Arming Extended | 20 | Auto Arming Time Extended By User | 33 | E464-GG-Ur### Auto Arm Time Extend | [CE] Closing Extended | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 103 | Armed By User | 13 | Armed By User- PIN | 18 | R401-GG-Ur### O/C By User | [CL] Closing Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 104 | Armed By Keyfob | 15 | Armed By User - Keyfob | 22 | R401-GG-Ur### O/C By User | [CL] Closing Report | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 105 | Armed By Token | 14 | Armed By User - Token | 21 | R401-GG-Ur### O/C By User | [CL] Closing Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 106 | Armed By Keyswitch | 18 | Armed By User - Keyswitch | 25 | R409-GG-Ur### Keyswitch O/C | [CS] Closing Keyswitch Zone/Point | P1 Zone | P2 Module | P3 | P4 | P5 | P6
O/C | 107 | Armed By Remote | 16 | Armed By Remote | 15 | R407-GG-Ur### Remote Arm/Disarm | [CQ] Closing Remote | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 108 | Armed By TimeZone | 17 | Armed By TimeZone | 17 | R403-GG-Ur### Automatic O/C | [CA] Automatic Close By Area | P1 TimeZone | P2 | P3 | P4 | P5 | P6 | User 0
O/C | 109 | Part Armed By User | 18 | Part Armed By User - PIN | 24 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 110 | Part Armed By Keyfob | 20 | Part Armed By User - Keyfob | 27 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 111 | Part Armed By Token | 19 | Part Armed By User - Token | 26 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 112 | Part Armed By Keyswitch | 23 | Part Armed By User - Keyswitch | 30 | E442-GG-Ur### Keyswitch Armed STAY | [NL] Perimeter Armed | P1 Zone | P2 Module | P3 | P4 | P5 | P6
O/C | 113 | Part Armed By Remote Part | 25 | Part Armed By Remote | 20 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 114 | Part Armed By TimeZone | 22 | Part Armed By TimeZone | 22 | E403-GG-Ur### Keyswitch Armed STAY | [NL] Perimeter Armed | P1+Text TimeZone | P2 | P3 | P4 | P5 | P6 | Legacy
O/C | 115 | Last To Arm | 11 | Last To Arm | 11 | R400-GG-Ur### Open/Close | [CL] Closing Report | P1+Text User | P2 | P3 | P4 | P5 | P6
Alarm | 116 | Keypad Fire Emergency | 21 | Keypad Fire Emergency | 21 | E110-GG-Zn### Fire | [FA] Fire | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 117 | Keypad Panic Emergency | 22 | Keypad Panic Emergency | 22 | E120-GG-Zn### Panic Alarm | [PA] Panic | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 118 | Keypad Medical Emergency | 24 | Keypad Medical Emergency | 24 | E100-GG-Zn### Medical | [MA] Medical | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 119 | Duress Alarm | 12 | Duress Alarm By User | 20 | E121-GG-Ur### Duress | [HA] Hold-Up | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 120 | Disarmed By User | 16 | Disarmed By User Ð PIN | 22 | E401-GG-Ur### O/C By User | [OP] Opening Report | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 121 | Disarmed By Keyfob | 18 | Disarmed By User - Keyfob | 25 | E401-GG-Ur### O/C By User | [OP] Opening Report | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 122 | Disarmed By Token | 17 | Disarmed By User -Token | 23 | E401-GG-Ur### O/C By User | [OP] Opening Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 123 | Disarmed By Keyswitch | 21 | Disarmed By User - Keyswitch | 28 | E409-GG-Ur### Keyswitch O/C | [OS] Opening Keyswitch | P1 Zone | P2 Module | P3 | P4 | P5 | P6
O/C | 124 | Disarmed By Remote | 18 | Disarmed By Remote | 18 | E407-GG-Ur### Remote Arm/Disarm | [OQ] Opening Remote | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 125 | Disarmed By TimeZone | 20 | Disarmed By TimeZone | 20 | E403-GG-Ur### Automatic O/C | [OA] Automatic Open | P1 User | P2 | P3 | P4 | P5 | P6 | User 0
O/C | 126 | First To Disarm | 15 | First To Disarm | 15 | E400-GG-Ur### Open/Close | [OP] Opening Report | P1+Text User | P2 | P3 | P4 | P5 | P6
System | 127 | User PIN Changed | 16 | User PIN Changed | 16 | Local | [JV] User Code Changed | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 128 | User PIN Deleted | 16 | User PIN Deleted | 16 | Local | [JX] User Code Deleted | P1+Text User A | P2 Console | P3+Text User2 | P4 | P5 | P6 | User A deleted a code for User B
System | 129 | User PIN Added | 14 | User PIN Added | 14 | Local | [JY] User Code Added | P1+Text User A | P2 Console | P3+Text User B | P4 | P5 | P6 | User A added a code for User B
System | 130 | User Token Added | 16 | User Token Added | 16 | Local | [DA] Card Assign | P1+Text User A | P2 Console | P3+Text User B | P4 | P5 | P6 | UserB added a Token for UserA
System | 131 | User Token Deleted | 18 | User Token Deleted | 18 | Local | [DB] Card Deleted | P1+Text User A | P2 Console | P3+Text User B | P4 | P5 | P6 | UserB deleted a Token for UserA
System | 132 | Valid Token Presented | 21 | Valid Token Presented | 21 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 133 | User Keyfob Added | 17 | User Keyfob Added | 17 | Local | Local | P1+Text User A | P2 Console | P3 | P4 | P5 | P6
System | 134 | User Keyfob Deleted | 19 | User Delete Keyfob | 18 | Local | Local | P1+Text User A | P2 Console | P3 | P4 | P5 | P6
System | 136 | TimeZone Data Changed | 21 | TimeZone Data Changed | 21 | E630-00-000 TimeZone Change | [JS] TimeZone Changed | P1+Text Timezone | P2+Text User | P3 Coinsole | P4 | P5 | P6
Alarm | 137 | High Temp Alarm | 15 | High Temperature Keypad Alarm | 29 | E158-00-Zn### High Temperature | [KA] Heat Alarm | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 138 | High Temp Alarm Restored | 24 | High Temperature Keypad Alarm Restore | 37 | R158-00-Zn### High Temperature Restore | [KR] Heat Restore | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 139 | Low Temp Alarm | 14 | Low Temperature Keypad Alarm | 28 | E159-00-Zn### Low Temperature | [ZA] Freeze Alarm | P1 Console | P2 | P3 | P4 | P5 | P6
Alarm | 140 | Low Temp Alarm Restored | 23 | Low Temperature Keypad Alarm Restored | 37 | R159-00-Zn### Low Temperature Restore | [ZR] Freeze Restore | P1 Console | P2 | P3 | P4 | P5 | P6
Trouble | 141 | Current Overload | 16 | Output Current Overload | 23 | E520-GG-ZN### Sounder/Relay Disabled | [OU] Output State Trouble | P1 Output | P2 Module | P3 | P4 | P5 | P6
Trouble | 142 | Current Normal | 14 | Output Current Overload Restored | 32 | R520-GG-Zn### Sounder/Relay Disabled | [OV] Output State Restore | P1 Output | P2 Module | P3 | P4 | P5 | P6
Trouble | 143 | Output Missing | 14 | Output Missing | 14 | E320-00-ZN### Sounder/Relay | [YA] Bell Fault | P1 Output | P2 Module | P3 | P4 | P5 | P6
Trouble | 144 | Output Restored | 15 | Output Restored | 15 | R320-00-ZN### Sounder/Relay | [YH] Bell Fault | P1 Output | P2 Module | P3 | P4 | P5 | P6
System | 145 | Output Off By User PIN | 22 | Output Turned Off By User PIN | 29 | Local | Local | P1 Output | P2 Module | P3+Text User | P4 | P5 | P6
System | 146 | Output On By User PIN | 21 | Output Turned On By User PIN | 28 | Local | Local | P1 Output | P2 Module | P3+Text User | P4 | P5 | P6
System | 147 | Output Off By TimeZone | 22 | Output Turned Off By TimeZone | 29 | Local | Local | P1 Output | P2 Module | P3+Text TimeZone | P4 | P5 | P6
System | 148 | Output On By TimeZone | 21 | Output On Turned On By TimeZone | 31 | Local | Local | P1 Output | P2 Module | P3+Text TimeZone | P4 | P5 | P6
System | 149 | Output Off Via RAS | 18 | Output Turned Off Via RAS | 25 | Local | Local | P1 Output | P2 Module | P3+Text User | P4 | P5 | P6
System | 150 | Output On Via RAS | 17 | Output Turned On Via RAS | 24 | Local | Local | P1 Output | P2 Module | P3+Text User | P4 | P5 | P6
Trouble | 151 | AC Power Fail - Mod | 19 | Expansion Module AC Power Fail Loss | 35 | E342-00-Zn### Exp Module AC Loss | [AT] AC Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 152 | AC Power Restore - Mod | 22 | Expansion Module AC Power Restored | 34 | R342-00-Zn### Exp Module AC Loss Restore | [AR] AC Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 153 | Module Lost | 11 | LAN Communication Lost To Module | 32 | E333-00-Zn### Expansion Module Fail | [EM] Expansion Device Missing | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 154 | Module Restored | 15 | LAN Communucation To Module Restored | 36 | R333-00-Zn### Expansion Module Restore | [EN] Expansion Device Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 155 | Exp Module Low Battery | 22 | Expansion Module Low Battery | 28 | E338-00-Zn### Exp. Module Low Battery | [YT] System Battery Trouble | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 156 | Battery Restored | 16 | Expansion Module Low Battery Restored | 37 | E338-00-Zn### Exp. Module Low Batt Restore | [YR] System Battery Restore | P1 Module | P2 Battery # | P3 | P4 | P5 | P6
Trouble | 157 | Overload | 8 | Current Overload | 16 | E330-00-ZN### Peripheral Trouble | [YI] Over-Current Trouble | P1 Output | P2 Module | P3 | P4 | P5 | P6
Trouble | 158 | Overload Restored | 17 | Current Overload Restored | 25 | R330-00-ZN### Peripheral Trouble Restore | [YJ] Over-Current Trouble Restore | P1 Output | P2 Module | P3 | P4 | P5 | P6
Trouble | 159 | IP Poll Failed | 14 | IP Network Poll Failed | 22 | E356-00-Zn### Loss Of Central Polling | [NT] Network Failure | P1 Module | P2 | P3 | P4 | P5 | P6 | Used for any IP network
Trouble | 160 | IP Poll Fail Restored | 21 | IP Poll Fail Restored | 21 | R356-00-Zn### Loss Of Central Polling Restore | [NR] Network Fail Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 161 | Module Trouble | 14 | Module Trouble | 14 | E330-00-ZN### Peripheral Trouble | [ET] Expansion Device Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 162 | Module Restored | 15 | Module Trouble Restored | 23 | R330-00-ZN### Peripheral Trouble Restore | [ER] Expansion Device Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Alarm | 163 | Module Tamper Alarm | 19 | Expansion Module Tamper | 23 | E341-00-Zn### Expansion Module Tamper | [ES] Expansion Device Tamper | P1 Module | P2 | P3 | P4 | P5 | P6
Alarm | 164 | Module Tamper Restored | 22 | Expansion Module Tamper Restored | 32 | R341-00-Zn### Exp. Module Tamper Restore | [EJ] Expansion Tamper Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 165 | Default PIN Trouble | 19 | Default Installer PIN or User 1 PIN Not Changed | 47 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 166 | RF Supervision Lost | 19 | RF Device Supervision Lost | 26 | E381-GG-Zn### Loss Of Supervision Ð RF | [BZ] Missing Supervision | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 167 | RF Supervision Restored | 23 | RF Device Supervision Restored | 30 | R381-GG-Zn### Loss Of Supervision Ð RF Restore | [BR] Burglary Restore | P1 Zone | P2 | P3 | P4 | P5 | P6
Trouble | 168 | RF Receiver Jam Detected | 24 | RF Receiver Jam Detected | 24 | E344-00-Zn### RF Receiver Jam Detect | [XQ] RF Interference | P1 Module | P2 Module | P3 | P4 | P5 | P6
Trouble | 169 | RF Receiver Jam Restored | 24 | RF Receiver Jam Restored | 24 | R344-00-Zn### RF Receiver Jam Detect Restore | [XH] RF Interference Restore | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 170 | RF Device Low Battery | 21 | RF Device Low Battery | 21 | E384-GG-Zn### RF Low Battery | [XT] Transmitter Battery Trouble | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 171 | RF Device Battery Restored | 26 | RF Device Low Battery Restored | 30 | R384-GG-Zn### RF Low Battery Restore | [XR] Transmitter Battery Restore | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Trouble | 172 | Rf Keyfob Low Battery | 21 | RF Keyfob Low Battery | 21 | E384-GG-Zn### RF Low Battery | [XT] Transmitter Battery Trouble | P1+Text User | P2 | P3 | P4 | P5 | P6
Trouble | 173 | Keyfob Battery Restored | 23 | RF Keyfob Low Battery Restored | 30 | R384-GG-Zn### RF Low Battery Restore | [XR] Transmitter Battery Restore | P1+Text User | P2 | P3 | P4 | P5 | P6
Alarm | 174 | Keyfob Panic Alarm | 18 | RF Keyfob Panic Alarm + P5 | 26 | E120-GG-Ur### Panic Alarm | [PA] Panic | P1+Text User | P2 | P3 | P4 | P5 | P6
Alarm | 175 | Senior Watch Alert | 18 | Senior Watch Alert Activated | 28 | E641-GG-000 Senior Watch Trouble | [QA] Emergency Alarm | P1 | P2 | P3 | P4 | P5 | P6
Alarm | 176 | Senior Watch Restored | 21 | Senior Watch Restored | 21 | R641-GG-000 Senior Watch Trouble | [QR] Emergency Alarm Restore | P1 | P2 | P3 | P4 | P5 | P6
Alarm | 177 | 24Hr Non Burg Zn Alarm | 22 | Alarm 24Hr Non Burglary Zone Alarm | 34 | E150-00-Zn### 24Hr Non Burglary | [UA] Untyped Zone Alarm | P1 Zone | P2 | P3 | P4 | P5 | P6
Alarm | 178 | 24Hr Non Burg Zn Restored | 25 | 24Hr Non Burg Zone Alarm Restored | 33 | R150-00-Zn### 24Hr Non Burglary | [UH] Untyped Zone Restore | P1 Zone | P2 | P3 | P4 | P5 | P6
System | 179 | RAS Session Begin | 17 | Remote Access Session Begin | 27 | Local | Local | P1 Method | P2 | P3 | P4 | P5 | P6 | Method=Direct, Modem, IP, GPRS
System | 180 | RAS Session Ended | 17 | Remote Access Mode End | 22 | Local | Local | P1 Method | P2 | P3 | P4 | P5 | P6 | Method=Direct, Modem, IP, GPRS
System | 181 | Unknown Token Presented | 23 | Unknown Token Presented | 23 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Access | 182 | Unknown PIN Entered | 19 | Unknown PIN Entered | 19 | Local | Local | P1 Console | P2 | P3 | P4 | P5 | P6
Access | 183 | User Logged On | 14 | User Logged On | 14 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Access | 184 | User Has Expired | 16 | User Has Expired | 16 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 185 | Communication Session | 21 | Communication Session | 21 | Local | Local | P1 Destination | P2 Module | P3 | P4 | P5 | P6
System | 186 | Handshake Error | 15 | Telco Handshake Error | 21 | Local | Local | P1 Destination | P2 Module | P3 | P4 | P5 | P6
Access | 187 | User Out Of Hours-Token | 23 | User Out Of Hours-Token Set | 28 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Access | 188 | User Out Of Hours-PIN | 21 | User Out Of Hours-PIN | 21 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Access | 189 | User Out Of Hours-Keyfob | 24 | User Out Of Hours-Keyfob | 24 | Local | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Access | 190 | Access Granted | 14 | Access Granted | 14 | E422-GG-Dr### Access Granted | [DG] Door Access Granted | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | B if Dual Custody
Access | 191 | Access Denied | 13 | Access Denied | 13 | E421-GG-Dr### Access Denied | [DD] Access Denied General | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | A=Failed User
System | 192 | Auto Arming Aborted | 19 | Auto Arming Aborted By User | 27 | E455-GG-Ur### Auto Arming Aborted | Local | P1+Text User | P2 Console | P3 | P4 | P5 | P6
Trouble | 193 | Date / Time Error Begin | 23 | The Date/Time is Incorrect | 26 | E626-GG-Zn### Time/Date Incorrect Begin | N/A | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 194 | Date / Time Error End | 21 | The Date/Time is now Correct | 28 | R626-GG-Zn### Time/Date Incorrect End | N/A | P1 Module | P2 | P3 | P4 | P5 | P6
Alarm | 195 | Fire Condition Begin | 20 | Fire Alarm Condition Begin | 26 | Local | Local | P1 | P2 | P3 | P4 | P5 | P6
Alarm | 196 | Fire Condition Ended | 20 | Fire Alarm Condition Ended | 26 | Local | Local | P1 | P2 | P3 | P4 | P5 | P6
Trouble | 197 | Low Voltage Reset | 17 | Low Voltage Reset | 17 | E339-00-Zn### Peripheral Reset | [RR] Power Up | P1 Module | P2 Table | P3 | P4 | P5 | P6 | Table: 0=Cold, 1=Warm, 2=Watchdog
Trouble | 198 | Watchdog Reset | 14 | Watchdog Reset | 14 | E339-00-Zn### Peripheral Reset | [RR] Power Up | P1 Module | P2 Table | P3 | P4 | P5 | P6 | Table: 0=Cold, 1=Warm, 2=Watchdog
Access | 199 | RAS Lockout - IP | 16 | RAS Lockout - IP | 16 | E413-GG-Ur998 Unsuccessfull Access | [RD] Remote Program Denied | P1+Text Machine Name | P2+Text IP= DL | P3 | P4 | P5 | P6 | Machine Name IP-Address DL-Direct Link
System | 200 | IP Network Disonnected | 22 | IP Network Disconnected | 23 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6
System | 201 | IP Network Connected | 20 | IP Network Connected | 20 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 202 | IP Address Conflict | 19 | IP Address Conflict | 19 | E362-00-Zn### IP Conflict | [NC] Network Condition | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 203 | IP Conflict Resolved | 20 | IP Address Conflict Resolved | 28 | R362-00-Zn### IP Conflict | [NR] Network Fail Restore | P1 Module | P2 | P3 | P4 | P5 | P6
O/C | 204 | Armed By Fingerprint | 20 | Armed By User - Fingerprint | 27 | R401-GG-Ur### O/C By User | [CL] Closing Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 205 | Part Armed By Fingerprint | 25 | Part Armed By User - Fingerprint | 32 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 Console | P3 | P4 | P5 | P6
O/C | 206 | Disarmed By Fingerprint | 23 | Disarmed By User - Fingerprint | 30 | E401-GG-Ur### O/C By User | [OP] Opening Report | P1+Text User | P2 Console | P3 | P4 | P5 | P6
System | 207 | User Fingerprint Added | 22 | User Fingerprint Added | 22 | Local | Local | P1+User User A | P2 Console | P3+Text User B | P4 | P5 | P6 | UserB added a Fingerprint for UserA
System | 208 | User Fingerprint Deleted | 24 | User Fingerprint Deleted | 24 | Local | Local | P1+Text User A | P2 Console | P3+Text User B | P4 | P5 | P6 | UserB deleted a Fingerprint for UserA
Access | 210 | Unknown Fingerprint | 19 | Unknown Fingerprint Presented | 29 | Local | Local | P1 Console | P2 | P3 | P4 | P5 | P6
Trouble | 213 | Sub Lan Module Lost | 19 | Sub Lan Module Lost | 19 | E333-00-Zn### Expansion Module Fail | [EM] Expansion Device Missing | P1 Module | P2 Class+ADD | P3 | P4 | P5 | P6 | Module=Door CTRL Number Class=Device Type ADD=Sub Lan Address
Trouble | 214 | Sub Lan Module Restored | 23 | Sub Lan Module Restored | 23 | R333-00-Zn### Expansion Module Restore | [EN] Expansion Device Restore | P1 Module | P2 Class+ADD | P3 | P4 | P5 | P6 | Module=Door CTRL Number Class=Device Type ADD=Sub Lan Address
Trouble | 215 | Sub Lan Module Trouble | 22 | Sub Lan Module Trouble | 22 | E333-00-Zn### Expansion Module Fail | [EM] Expansion Device Missing | P1 Module | P2 Class+ADD | P3 | P4 | P5 | P6 | Module=Door CTRL Number Class=Device Type ADD=Sub Lan Address
Trouble | 216 | Sub Lan Module Trbl Rest | 24 | Sub Lan Module Trouble Restored | 31 | R333-00-Zn### Expansion Module Restore | [EN] Expansion Device Restore | P1 Module | P2 Class+ADD | P3 | P4 | P5 | P6 | Module=Door CTRL Number Class=Device Type ADD=Sub Lan Address
Trouble | 217 | Sub Lan Module Overload | 23 | Sub Lan Module Current Overload | 31 | E312-00-Zn### Power Supply Over Current | [YI] Over Current Trouble | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 218 | Sub Lan Mod Overload Rest | 25 | Sub Lan Module Current Overload Restored | 40 | R312-00-Zn### Power Supply Over Current Restore | [YJ] Over Current Trouble Restore | P1 Module | P2 | P3 | P4 | P5 | P6
System | 219 | RAS Refused IP Address | 22 | RAS Refused IP Address | 22 | Local | Local | P1 Method | P2 Text IP Addr | P3 | P4 | P5 | P6 | Method=Direct, Modem, IP, GPRS
System | 220 | RAS Refused Busy | 16 | RAS Session Refused Busy | 24 | Local | Local | P1 Method | P2 Text CLI/IP | P3 | P4 | P5 | P6 | Method=Direct, Modem, IP, GPRS
System | 221 | RAS Terminated By Alarm | 23 | RAS Terminated By Alarm | 23 | Local | Local | P1 Method | P2 | P3 | P4 | P5 | P6 | Method=Direct, Modem, IP, GPRS
System | 222 | RAS Terminated By Report | 24 | RAS Terminated By Pending Report | 32 | Local | Local | P1 Method | P2 | P3 | P4 | P5 | P6
O/C | 225 | Part Armed By iFob | 18 | Part Armed By iFob | 18 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1+Text User | P2 Mobile | P3 | P4 | P5 | P6 | We should include the Phone it came from
O/C | 226 | Disarmed By iFob | 16 | Disarmed By iFob | 16 | E401-GG-Ur### O/C By User | [OP] Opening Report | P1+Text User | P2 Mobile | P3 | P4 | P5 | P6 | We should include the Phone it came from
O/C | 227 | Armed By iFob | 13 | Armed By iFob | 13 | R401-GG-Ur### O/C By User | [CL] Closing Report | P1+Text User | P2 Mobile | P3 | P4 | P5 | P6 | We should include the Phone it came from
Trouble | 228 | Zone Lockout Restored | 21 | Zone Lockout Restored | 21 | R575-GG-Zn### Burglary Bypass Restore | [BE] Swinger Trouble Non Fire | P1 Zone | P2 Module | P3 | P4 | P5 | P6
O/C | 229 | End Of Exit | 11 | End Of Exit | 11 | Local | Local | P1 | P2 | P3 | P4 | P5 | P6
System | 230 | TimeZone Begin | 14 | TimeZone is now TRUE | 20 | Local | Local | P1 TimeZone | P2 | P3 | P4 | P5 | P6
System | 231 | TimeZone End | 12 | TimeZone is now FALSE | 21 | Local | Local | P1 TimeZone | P2 | P3 | P4 | P5 | P6
System | 255 | DC Too Low - No Start | 21 | DC Voltage Is Too Low No Start | 30 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6 | The Voltage is too low for module to start.
System | 256 | Firmware Upgraded | 17 | Module Firmware Upgraded | 24 | Local | Local | P1 Module | P2 Old R. | P3 New R. | P4 | P5 | P6 | New Firmware has been installed. Old/New Revision
Trouble | 258 | Memory Fault | 12 | System Memory Fault | 19 | E304-00-Zn### ROM Checksum Bad | [YF] Parameter Checksum Fail | P1 Module | P2 | P3 | P4 | P5 | P6
O/C | 259 | Guard Tour Begin | 16 | Guard Tour Begin | 16 | E466-GG-Ur### Service On Premises | [JP] User On Premises | P1+Text User | P2 | P3 | P4 | P5 | P6
O/C | 260 | Guard Tour End | 14 | Guard Tour End | 14 | R466-GG-Ur### Service Off Premises | N/A | P1+Text User | P2 | P3 | P4 | P5 | P6
Trouble | 261 | User Test Required | 18 | User Test Required (Walk Test Due) | 34 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 262 | User Test Completed | 19 | User Test Completed | 19 | Local | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | 263 | Exit Error Restored | 19 | Exit Error Restored | 19 | R374-GG-Zn### Exit Error Restore | Local | P1 Zone | P2 Module | P3 | P4 | P5 | P6
Alarm | 266 | RF Receiver Tamper | 18 | RF Receiver Tamper Alarm | 24 | E341-00-Zn### Expansion Module Tamper | [XS] RF Receiver Tamper | P1 Module | P2 | P3 | P4 | P5 | P6
Alarm | 267 | RF Receiver Tamper Rest | 23 | RF Receiver Tamper Restored | 27 | R341-00-Zn### Exp. Module Tamper Restore | [XJ] RF Receiver Tamper Restoral | P1 Module | P2 | P3 | P4 | P5 | P6
O/C | 270 | Disarmed By Macro | 17 | Disarmed By Macro | 17 | E403-GG-Ur### Automatic O/C | [OA] Automatic Open | P1 User | P2 | P3 | P4 | P5 | P6 | User 0
O/C | 271 | Armed By Macro | 14 | Armed By Macro | 14 | R403-GG-Ur### Automatic O/C | [CA] Automatic Close By Area | P1 Macro | P2 | P3 | P4 | P5 | P6 | User 0
O/C | 272 | Part Armed By Macro | 19 | Part Armed By Macro | 19 | E441-GG-Ur### Armed In STAY | [NL] Perimeter Armed | P1 Macro | P2 | P3 | P4 | P5 | P6 | User 0
Access | 501 | Requested Arm/Disarm | 20 | Requested Control Panel to Arm or Disarm Area | 45 | Local | Local | P1 Area State | P2 Area Number | P3 | P4 | P5 | P6 | Internal event Only
Access | 524 | Learned Credentials | 19 | Learned Credentials | 19 | Local | Local | P1 0-1Byte | P2 2-3Byte | P3 4-5Byte | P4 6-7Byte | P5 | P6 | Internal event Only
Access | 525 | Software Asserted | 17 | Software Asserted | 17 | Local | Local | P1 Hex | P2 Hex | P3 Hex | P4 Hex | P5 Hex | P6 Hex | Internal event only
Access | 526 | Door Locked By User | 19 | Door Locked By User Command | 27 | Local | Local | P1 Door | P2+Text User | P3 | P4 | P5 | P6
Access | 527 | Door Unlocked By User | 21 | Door Unlocked By User Command | 29 | Local | Local | P1 Door | P2+Text User | P3 | P4 | P5 | P6
Access | 528 | Door Locked By TimeZone | 23 | Door Locked By TimeZone | 23 | Local | Local | P1 Door | P2+Text TimeZone | P3 | P4 | P5 | P6
Access | 529 | Door Unlocked By TimeZone | 25 | Door Unlocked By TimeZone | 25 | Local | Local | P1 Door | P2+Text TimeZone | P3 | P4 | P5 | P6
Access | 530 | Door Overriden | 14 | Door has been Overriden In Locked State | 39 | Local | [DC] Door Access Closed | P1 Door | P2+Text User | P3 | P4 | P5 | P6
Access | 531 | Door Override Cancelled | 23 | Door Override Now Cancelled | 27 | Local | [DN] Door Access Open | P1 Door | P2+Text User | P3 | P4 | P5 | P6
Access | 532 | Door Unlocked - Fire | 20 | Door Unlocked - Fire" | 21 | Local | Local | P1 Door | P2 Input | P3 | P4 | P5 | P6
Access | 533 | Door Unlocked Restore | 21 | Door Unlocked Fire Restored | 27 | Local | Local | P1 Door | P2 Input | P3 | P4 | P5 | P6
Access | 534 | Door Input Event | 16 | Door Input Event | 16 | Local | Local | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 535 | Door Input Event Restored | 25 | Door Input Event Restored | 25 | Local | Local | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 536 | Door Open Too Long | 18 | Door Open Too Long Alarm | 24 | E426-GG-Dr### Door OTL | [DN] Door Left Open Too Long | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 537 | Door Open Too Long Restore | 26 | Door Open Too Long Alarm Restored | 33 | R426-GG-Dr### Door OTL | [DH] Door Left Open Restore | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 538 | Door Forced Open | 16 | Door Forced Open Alarm | 22 | E423-GG-Dr### Door Forced | [DF] Door Forced Open | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 539 | Door Forced Restored | 20 | Door Forced Open Alarm Restored | 31 | R423-GG-Dr### Forced Restore | [DR] Door Restoral | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 544 | Door Latch Trouble | 18 | Door Latch Trouble | 18 | E427-GG-Dr### Monitor Trouble | [DT] Access System Trouble | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 545 | Door Latch Trbl Restored | 24 | Door Latch Trouble Restored | 27 | R427-GG-Dr### Monitor Restore | [DR] Door Restoral | P1 Door | P2 | P3 | P4 | P5 | P6
Access | 548 | Access Count Reached | 20 | Access Count Reached | 20 | Local | Local | P1 Region | P2 Door | P3 | P4 | P5 | P6
Access | 549 | Access Count Within Limits | 26 | Access Count Within Limits | 26 | Local | Local | P1 Region | P2 Door | P3 | P4 | P5 | P6
Access | 551 | Access Denied - Out Of Hrs | 26 | Access Denied User is Out of Hours | 34 | E421-GG-Dr### Access Denied | [DP] Access Denied Unauthorised Time | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | A=Failed User
Access | 552 | Access Denied - Expired | 24 | Access Denied User Has Expired | 30 | E421-GG-Dr### Access Denied | [DP] Access Denied Unauthorised | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | A=Failed User
Access | 553 | Access Denied - Area Armed | 26 | Access Denied Area Is Still Armed | 33 | E421-GG-Dr### Access Denied | [DQ] Access Denied Unauthorised Arming State | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | A=Failed User
Access | 554
Access | 555
Access | 556
Access | 557 | Denied Interlocking | 20 | Access Denied Due to Interlocking | 33 | E421-GG-Dr### Access Denied | [DW] Access Denied Interlock | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6 | Door 2 was still open
Access | 558 | Counter Limit Exceeded | 23 | Access Denied Counter Limit Exceeded | 36 | E421-GG-Dr### Access Denied | [DD] Access Denied General | P1 Door | P2+Text User | P3 Console | P4 | P5 | P6
Access | 559 | Access Denied Unknown | 22 | Access Denied Reason Unknown | 28 | E421-GG-Dr### Access Denied | [DD] Access Denied General | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6
Access | 560 | Access Denied Passback | 22 | Access Denied Passback | 22 | E421-GG-Dr### Access Denied | [DI] Access Denied Passback | P1 Door | P2+Text User | P3 Console | P4 | P5 | P6
Access | 561 | Dual Credential Timeout | 24 | Access Denied Dual Credential Timeout | 37 | E421-GG-Dr### Access Denied | [DD] Access Denied General | P1 Door | P2+Text User | P3 Console | P4 | P5 | P6
Access | 566 | Invalid Door Group | 18 | Access Denied Invalid Door Group | 32 | E421-GG-Dr### Access Denied | [DD] Access Denied General | P1 Door | P2+Text User A | P3+Text User B | P4 Console | P5 | P6
Access | 567 | Egress Denied | 14 | Door Access Denied Via Egress | 29 | E424-GG-Dr### Egress Denied | [DD] Access Denied General | P1 Door | P2 Console | P3 | P4 | P5 | P6 | No need for OOH
Access | 568 | Egress Granted | 15 | Door Access Granted Via Egress | 30 | E425-GG-Dr### Egress Granted | [DX] Egress Granted | P1 Door | P2 Console | P3 | P4 | P5 | P6
Trouble | ??? | Self Test Restore-Mod | 21 | Expansion Module Self Test Fail Restored | 40 | R343-00-Zn### Exp. Module Self Test Fail Restore | Local | P1 Module | P2 | P3 | P4 | P5 | P6
Trouble | ??? | Self Test Fail-Mod | 19 | Expansion Module Self Test Failed | 33 | E343-00-Zn### Exp. Module Self Test Fail | [YU] Exp Device Diagnostic Error | P1 Module | P2 | P3 | P4 | P5 | P6